No.296/T2/19/KSFDC		      				                30.01.2019

Quotation notice for  2 KVA  online  UPSs

1.	 Item rate quotations are invited for 2 KVA online uninterrupted power supply system(UPSs) of following specifications at Kalabhavan Digital Studio, Thiruvananthapuram. Quotationer may quote rate for the supply, installation, testing and commissioning.

1. 	2 KVA

Supply, installation, testing and commissioning of 2 KVA, single phase input, 230V out put UPS IGBT Based online UPS with inbuilt isolation transformer with tubular battery for a back up of 45 minutes (8 Nos. of 42 AH approximately) with battery stand and interconnecting cables and leak proof fibre glass tray.

(Refer technical specification & schedule )

2.	Recommended brands of batteries

Exide

3.     Only original equipment manufacturers and their authorized dealers need to quote. They shall have adequate service centers near to the theatres concerned. They shall have adequate number of installations to their credit. These are eligibility conditions. The quotationer shall be amenable to techno commercial discussions.

4.	The rate quoted shall be inclusive of all taxes & rates.  GST number of both the parties to be shown in invoice specifically.

5.	The tender shall hold firm for period of six months. The exact requirement of numbers of UPSs will be given at the time of issuing purchase order.  The supply installationtesting & commissioning shall be completed within 15 days from the date of Purchase order.

6.	After the issue of purchase order, quotation may execute an agreement on stamp paper worth Rs.200/- before delivery of items for installation. 5% of the total order value will be submitted as security deposit till the expiry of defect liability period.

7.	Security deposit will be released only after the defect liability period which shall be 3 years from the date of successful installations.

8.	Minimum 3 years warranty for UPS & 4 years for battery  may be provided.

9.	Post warranty AMC rates also can also  be quoted separately.

10.	Address of the nearest service center also may be indicated.

11.	Quatationer  may enclose a list of their installations in Kerala.

12.	Product catalogue and data sheets may be enclosed.

13	The specifications of the product may be separately shown along with the rates.

14.	Quotations with rates for UPS with specifications as attached  with all enclosures as requested by this notice in sealed covers superscribing "QUOTATION FOR UPS" shall reach Managing Director, Chalachithra Kalabhavan, Vazhuthcaud, Thiruvananthapuram-14 not later than 3.00pm on       11.02.2019. Quotations will  be opened on the same day at 3.30pm in the presence of available quotationers.

15. 	Payment will be made only after deliver and successful installation and certification there to.

16.	MD, KSFDC reserves the right to reject any or all tenders without assigning any reason whatsoever.

17.	A copy of this tender notice in full may be enclosed duly signed with seal to comply with these conditions.

18	Quotationer shall comply with the deliver/ schdule as noticed by KSFDC if the quotaion is accepted.

19.	All statutory deductions as applicable will be effected.

Managing Director

SUPPLY OF UPS SYTEM FOR KSFDC.

IEC 61000-3-2 OR EQUIVALENT IS SPECIFICATION

- TECHNICAL SPECIFICATION

1.1 Type Static

1.2 Power rating at load PF 0.9 lagging or above2000VA/1800W

1.3 Application For Induction/SMPS loads

1.4 Quantity Refer Power distribution scheme/BOQ

1.5 Method of energy storage Electrical – battery back-up

1.6 Designation Static Bypass

1.7Whether transfer switch requiredfor secondary Back-upRequired(Static switches for uninterruptedtransfer of loads from inverter toregulated supply)

1.8 Installation Indoor, ACventilated

2.0 Enclosure

2.1 Material Cold rolled sheet steel

2.2 Sheet thickness (mm) 2

2.3 Degree of protection as per IS-2417 IP-31

2.5 Cable entry Top

2.6 Acoustic noise level<= 50db

3.0 UPS system

3.1 Input- Supply voltage V240 V, 1 ph, 50hz AC effectivelyearthed

3.2 Output

3.2.1 Output voltage 230V, 1ph, 50hz AC.

3.2.2AC voltage accuracy (steady state)over entire load

3.2.3 Transient voltage regulation % 8 at 100% load step

3.2.4 Transient recoveryReturn to steady state condition within50ms after disturbance

3.2.5 Voltage wave form Sinusoidal

3.2.6Range of adjustment of ac outputvoltage% 5 at rated load

3.2.7 AC harmonic content % 5 total, 3 for any single harmonic

3.2.8 Phase displacement

3.2.9 Nominal frequency Hz 50

3.2.10 Frequency regulation % 0.5

4.0 DC link (battery)

4.1 No. of 100% capacity batteries

4.2 Type of battery cell - Tubular

4.3 Battery support time Min 30 (Offline) & 15 (Online)

5.0 Battery charger (Rectifier unit)

5.1 No. of units Two

5.2 Rectifier unitSilicon rectifier, single phase full wave /three phase full wave

5.3 Type Float cum boost charger

5.4 Recharge time on boost charge Hrs 8

5.5 In rush current

Maximum 25% of full load current

(energizing rectifier transformer with

inverter at no load)

6.0 Inverter

6.1 No. of 100% inverters in system Two

6.2 Type of power switching deviceThyristers / power transistors

6.3 Current capacity As per system requirement

6.3.1 Overload % 125 for 10 min. & 150 for 10 secs.

6.3.2 Short time withstand % 500 for 5 milli seconds.

6.3.3 Over current setting range %100 to 300 of load current, fieldadjustable

6.3.4Synchronizing Between inverters andStandby supplyNot required.

6.4Master / follower synchronizingsystemNot required.

7.0 Static switch

7.1 Type Static

7.2 No. of switches Two

7.3 RatingEqual to UPS output kVA rating at 0.99pf

7.4 Nominal frequency Hz 50

7.5 PurposeStatic interrupter / static load transfer tostandby regulated supply

7.6 Maximum transfer time Maximum of ¼ cycle

7.7 Short time rating for one sec. % 750

7.8 Whether make before break Yes

9.0 Circuit breaker

9.1 For use in ac system

9.1.1 Type MCCB/ MCB / RCBO

9.1.2 Application V/Ph240, 1ph + N

9.1.3 Quantity Refer Single line diagram

9.1.4Rating – current short time ratingfor one sec.kA

9.1.5 Protection setting range50% to 200 % overload,200% to 800% short circuit release

9.1.6 Operation Manual

9.2 For use in DC system

9.2.1 Type Air break

9.2.2 Application Battery

9.2.3 Quantity 2

9.2.4 Rating (Tenderer to state)

9.2.5 Protection, setting range50% to 200% overload,200% to 800% short circuit releaseA.

10.Installation Operation Manual shall be furnished and shall include as a minimum the following:

1.	Safety instructions

2.	System description, specifications and control

3.	Installation planning

4.	Installation and start-up

5.	Operational guide

6.	Control panel reference

7.	Warranty and service information

8.Order of preference:

9.    GE,UNICORN ,APC,EPI,SOCOMEC,DELTA, TECHSER

10   Warranty Period :Minimum 3 years for UPS and 4 years for batteries

# PROJECT: KSFDC-Kalabhavan Digital studio at Trivandrum:

# SUPPLY OF UPS

| Sl.No. | Description | Qty |
| --- | --- | --- |
| 1. | Each system consist 100% capacity IGBT rectifier and 0.99 Input PF and above 0.90 out put PF. Supply of 1 phase, 50c/s, and 1 phase in and 1 phase output UPS system with 45 minutes backup(8 nosof 42 AH approximately)equipped withIGBT Based online Ups with Isolation transformer, "ALARM" for mains supply failure & Alarm Mute switch and withRequired nos: of tubular batteries, stand, interconnecting cables and leak proof fibre glass tray.etc. complete. 2 KVA UPS | 1set |

Note: The tenderer is required to include  the cost of all other items which in case are not included but are essentially  required for successful commissioning of the system.  2. The quoted amount shall be net inclusive of all taxes and duties for the delivery at the site.

Date:									(SIGNATURE OF THE TENDERER)