## schedule
KERALA STATE FILM DEVELOPMENT CORPORATION LTD, THIRUVANATHAPURAM.
Name of Work: HVAC works ( High side, Air disribution work & Low side) of Kalabhavan Digital studio at Trivandrum.
SCHEDULE
Sl. no. | Description | Qty | Unit | Rate (INR) | Amount (INR)
A) HIGH SIDE
1 | DX SYSTEM
1.1 | DUCTED TYPE SPLIT A/C
Supply, Installation testing and commissioning of Ducted type split/package air cooled Air-conditioners each complete with scroll compressor, air cooled condenser and evaporator with copper tubes, GSS casing, filters, cooling coils, fan motors, control wiring, refrigerant controls and accessories, including MICRO-PROCESSOR CONTROL with indication lamps for the operation of the system with thermostat fixed in the respective rooms to adjust the temperature according to the equipments requirements with Micro- processor control panel for each machine.
Bidder to elaborate the features of Micro- processor panel. Making good of civil work's during installation.Bidder shall be quoted with spring type vibration isolators for indoor units for arresting the vibration transferring to the floors.
The quote should be inclusive of control cabling from machine out door unit to indoor unit and from from DB to indoor unit power cabling along with earthing. This shall facilitate all functions such as ON OFF thermostat to compressor control, fan interlocks, HP/LP & AFT controls etc. And MS base frame for outdoor units complete with epoxy painting, vibration isolation pads, supports, hangers, railing, brackets etc including civil works. Note: Apply 2 coats of epoxy primer and 2 coats of black paint, Each air conditioner unit should be provided with 5 Rmt. of copper piping between Indoor unit to outdoor unit as spesified in (1.3) Refrigerant piping.
The refrigerant shall be eco-friendly gasses like HFC or latest, These eco friendly refrigerants shall be with zero Ozone depleting substances. The quote shall be inclusive of supply air canvas and return air canvas connection to pleanum box. (NOTE: Inside noise level of the dubbing hall & console after installation shall meet NC-25 standards)
1.2 | 3.0 TR - Ceiling suspended inverted type Ducted system (400 CFM/TR) | 1 | Nos
1.3 | REFRIGERANT PIPING
Installation and commissioning of hard/soft copper refrigerant piping, complete with 10mm thick closed cell Class O Nitrile Rubber Insulation , fittings, elbows, bends, supporting and clambing arrangement on walls, cable trays/trenches including necessary civil works.
Refrigerant piping to be measured based on the distance between the indoor and outdoor units irrespective of number of circuits. The piping will be measured as one length for suction and liquid line. Insulation will be measured along with the piping and not be claimed as extra.(eg:- Ref. Ppg in bunches –17 TR AC Unit with 2 Nos. 8.5 TR Compressors and 1 RMT of 2 sets of Ref Pipes ie, 4 Nos. Pipes in all considered as 1 RMT ) FOR MACHINES HAVING PIPE LENGTH LONGER THAN 20 MTS, RESIZE USING LARGER DIA.
1.3.1 | 3.0 TR - Ducted type (400 CFM/TR) | 5 | Rmt
1.4 | DRAIN PIPING:
Supply, installation, testing & commissioning of following sizes. insulated PVC drain pipe' from AHU drain pans to nearest floor drain complete with interconnection, flanges, elbows, tees, nuts, U-trap etc. The insulation shall be 6 mm thick closed cell Class O Nitrile Rubber foam insulation.
1.4.1 | 32mm dia. | 1 | Rmt
1.4.2 | 25mm dia. | 5 | Rmt
B) AIR DISTRIBUTION WORKS:
2 | AIR DISTRIBUTION WORKS:
2.1 | SHEET METAL WORKS:
2.1.1 | Supply, Fabrication,installation,testing &commissioning of Site fabricated GSS ducting complete with splitter dampers, turning vanes, access doors, supports, etc Ducting to be as per SMACNA standards. Galvanizing shall be class VII-light coating of zinc, nominal 120 gm/sq.m and lock forming quality prime material.
All exposed duct work should be thermaly insulated with 50mm thick 24kg/m3 TF quality expanded polystyrene
All the supports of the duct will be painted to match the ducting/aesthetic
2.1.1.1 | 22 Gauge (0.8MM) | 1 | Sqmtr
2.1.1.2 | 24 Gauge (0.63MM) | 2 | Sqmtr
2.2 | Supply, Installation, testing, commissioning and balancing of GSS powder coated fresh air/exhaust air louver with 4 side flanges, Bird netscreen, damper arrangement and as per approved colour shade by the architect. | 0.4 | Sq.mtr.
2.3 | Supply, installation, testing and commissioning of multi blade opposed blade GSS dampers for ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system . | 0.6 | Sq.mtr.
C) LOWSIDE
3 | THERMAL & ACOUSTIC INSULATION: - low side
3.1 | Supply Installation, Testing and commissioning of Supply Duct insulation 13 mm thick closed cell elastomeric nitrile foam rubber insulation class Stuck to duct as per specifications
Thermal insulation material for ducts shall be 13mm closed cell elastomeric non polar UV resistant-UL94-Class-O and Nitrosmine free. Nitrile Rubber/EPDM of thermal conductivity of the insulation material shall not exceed 0.038 W/m K at an average temperature of of 30 degC.
| Density of nitrile rubber shall be 40-60 Kg/m3. The product shall have temperature range of -40 deg C to 105 deg C. The insulation material shall be fire rated for Class O as per BS 476 Part 6: 1989 for fire propagation test and for Class 1 as per BS 476 Part 7,1987 for surface spread of flame test. Water vapor permeability shall not less then 0.024 per inch ( 2.48x10-14 Kg/m.s Pa ) as per DIN 53122 part DIN 52615. | 1 | Sq.mtr.
3.2 | Supply Installation, Testing and commissioning of Supply Duct/ Room acoustic insulation 10/20 mm thick open cell elastomeric nitrile foam rubber insulation class Stuck to duct as per specifications
Acoustical insulation material for ducts shall be 10 and room shall be 20 mm open cell elastomeric non polar – UV resistant-UL94-Class- O - and Nitrosmine free. Nitrile Rubber/EPDM of thermal conductivity of insulation material shall not exceed 0.046 W/m K at an average temperature of of 30 degC. Density of nitrile rubber shall be 120-140 Kg/m3.
The product shall have temperature range of -40 deg C to 105 deg C. The insulation material shall be fire rated for Class 1 as per BS 476 Part 7: (1989 for fire propagation test and for Class 1 as per BS 476 Part 7,1987 for surface spread of flame test.) Water vapor permeability shall not less then 0.024 per inch ( 2.48x10-14 Kg/m.s Pa ) as per DIN 53122 part DIN 52615.
3.2.1 | 13 MM Nitrile Rubber | 1 | Sqmtr
3.2.2 | 20 MM Nitrile Rubber (RO) | 1 | Sqmtr
3.3 | Supply and connecting canvas | 1 | lot
3.4 | Dismantling of existing air conditioner unit and connected copper and drain pipes. | 1 | Lot
3.5 | Supply and laying of XLPE insulated sheathed armoured LT 1.1KV grade aluminium conductor cable /AYFYof following sizes with clamps over all conforming to IEC60364-5-523/ IS:1554 4CX10 sqmm AL cable (VDB to O/D unit) | 25 | Rmt
3.6 | Supply and end termination with brass compression gland and aluminium lugs for following mentioned cables including gland earthing etc. complete. 4 x 10 sq.mm | 2 | Nos
3.7 | Supply and fixing of out door type syntex box with din rail suitable for fixing 4P isolator. | 1 | Nos
| TOTAL |  |  | Rs.
In Words
ANNUAL MAINTANANCE CONTRACT
1 | Annual maintenance contract charges including spares, gas and consumables for the above plant per year for 4 years on per ton basis and percentage increase every year for 4 years after warranty period of 1 year. The frequency of servicing shall be once in 3 months every year for routine service and immediate on break down calls. | TONNAGE
1) | 1ST YEAR
2) | 2ND YEAR
3) | 3RD YEAR
4) | 4TH YEAR