## Sheet1
KERALA STATE FILM DEVELOPMENT CORPORATION LTD
Shedule for supply connection of 50 kVA generator at Chitranjali Studio
| Description | Qty | Unit | Rate | Amount
1 | Supply, Fabrication, installation, testing and commissioning of 100A LT panel board dust tight, vermin proof, wall fixing, front operated cubicle construction with three compartments complete with hinged and earthed front doors with name plate, legend plate, danger notice board, heavy duty rubber gaskets, removable gland plates made out of 3mm thick sheet steel., Size 90 cmX45 cm(LXB). The board shall be fabricated out of 16 SWG CR sheet and powder coated with shade RAL 7032 after phosphating. Control wiring to be done using copper wire 4 sq.mm for CT's and 2.5 sq.mm copper wire for rest of the circuit. Panel to be fabricated as per CPRI approval. Suitable rating cable can be used for connecting load change over switch and MCB
100 A, 4 pole cubicle type On Load change over switch (make L&T or equivalent)
Metering Instruments & Indications
Analogue Ammeters with range 0-100A with accuracy CL 0.5 and with control fuses – 3 Nos.
CTs – ratio 100/5A CL 0.5 Burden 15 VA – 3 Nos
Analogue Voltmeter 0-500 V with selector switch for three line display accuracy CL 1 and with control fuses– 1 No.
Frequency meter -- 1No
RYB phase indicating lamps (lamps shall be of LED) with control fuses/ mcb – 2 sets with toggle switch
63 A four pole (3ph & N) 415 volts MCB
Flush mount Digital kWh meter 3Ph 4 Wire 5A
|  | 1 | No
2 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
| 3.5 X 120 sq mm armoured Aluminium UG cable | 12 | Mtr
| 3.5 X 35 sq mm armoured Aluminium UG cable | 5 | Mtr
3 | Providing and fixing 25 mm X 3 mm copper strip on surface or in recess for connections and connecting the strip to the old existing strip with nut, bolt, spring, washer, applying lead soldering etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass/steel nut bolt & spring washer spaced at 50mm) as required | 7 | Mtr
4 | Excavating trench of 10" width & 1 feet depth for laying pipes, cables etc including excavation,getting out the excavated soil, supplying and laying three meter length 6" PVC pipe in the trench, and filling the trench with required soil and finishing the surface using cement concrete and making good the same etc as required. |  | LS
5 | Supplying and making end termination with brass compression gland and aluminium lugs with earthing for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
| 3.5 X 120 sq mm armoured Aluminium UG cable | 2 | No
| 3.5 X 35 sq mm armoured Aluminium UG cable | 2 | No
Total